## B&M
2021 EQUIPMENT HAZARDS RISK EVALUATION GUIDE
| This Risk Evaluation Guide is designed to serve as a guide to identify the most common exposures present at a CEMEX plant. While most hazards are captured here, there may be site-specific hazards at any plant that are not captured here but nevertheless present a property and/or business interruption potential. These are presented on the FM Global Risk Report and should be discussed between plant personnel and FM Global Field Engineers to fully understand both the hazard and solution. Further information on these hazards is available through FM Global Data Sheets which are listed under the Resources at the right column. |  | Resources. All are available FREE at:
www.fmglobalcatalog.com
www.fmglobaldatasheets.com
Line No. | (Note: additional comments are inserted as "Comments" as viewed through Excel or printed with Comments.) |  | Data Sheets | UTH | Other
| MECHANICAL PREVENTIVE MAINTENANCE |  | 17-17 Mining and Ore Processing
17-0 Maintenance and Inspection
| ROTARY KILNS | FREQUENCY
10 | Alignment on all kilns - as experience dictates, but considering the recommended frequency | Alignment: 2 yrs | 6-17 Rotary Kilns | UTH Rotary Kilns
11 | Shell ovality on all kilns - as experience dictates, but considering the recommended frequency | Ovality: Annually | 6-17 Rotary Kilns | UTH Rotary Kilns
12 | N.D.E. ring gear, pinion and its shaft, carrying rollers and their shafts | 3 yrs | 17-1 NDE
13 | Test dedicated Emergency I.C. Engine Generator or D.C. pony motor drive | Weekly | 6-17 Rotary Kilns
14 | Spare ring gear or acceptable contingency plan |  | 13-7 Gears | UTH Gear Failure
15 | Spare riding ring (tire) or acceptable contingency plan
16 | Spare pinions, shafts, and drive gears or acceptable contingency plans
17 | Temperature monitoring system for trunnion bearings
18 | Drive gearbox: temperature protection and/or low oil pressure and loss of oil flow if applicable
19 | Operator training program |  |  | UTH Operator Training
| RAW MILLS | FREQUENCY
22 | Vibration analysis program and oil analysis | Vibration: Weekly Oil: Quarterly | 17-4 Vibration | UTH Vibration
23 | Undercover gearbox inspections | 3 yrs
24 | High vibration trip for enclosed gearsets |  | 13-7 Gears
25 | N.D.E. of gears (ring gear and pinion) | 3 yrs | 17-1 NDE | UTH Gear Failure
26 | High temperature alarm and trip for the main bearings of critical high-speed enclosed gearboxes
27 | Drive gearbox: high oil temperature, low oil pressure and low oil level alarms and trips for critical high-speed enclosed gearboxes
28 | Spare motor, pinion, ring gear, and/or drive gearbox components or adequate contingency plans |  | 5-17 Motors | UTH Electrical Testing of Motors
| FINISH MILLS | FREQUENCY
31 | Vibration analysis program and oil analysis | Vibration: Weekly Oil: Quarterly | 17-4 Vibration | UTH Vibration
32 | Undercover gearbox inspections | 3 yrs
33 | High vibration trip for enclosed gearsets |  | 13-7 Gears
34 | N.D.E. of gears (ring gear and pinion) | 3 yrs | 17-1 NDE | UTH Gear Failure
35 | High temperature alarm and trip for the main bearings of critical high-speed enclosed gearboxes
36 | Drive gearbox: high oil temperature, low oil pressure and low oil level alarms and trips for critical high-speed enclosed gearboxes
37 | Spare motor,pinion, ring gear, and/or drive gearbox components or adequate contingency plans |  | 5-17 Motors | UTH Electrical Testing of Motors
HOUSEKEEPING (Good Engineering Practices)
40 | Switchgear and Motor Control Centers (MCC)/ keep rooms clean, cool, dry and free of miscellaneous objects |  |  | UTH Corrosion Vessels & Pipes
41 | Cement dust kept to a minimum around bearings and motors of Raw and Finish Mills and conveyors
| ID, FD, PREHEATER, KILN, RAW & FINISH MILL FANS 1500 HP/1100-kW and above | FREQUENCY
44 | N.D.E. of critical components (hubs and fan blades) | 2 yrs | 17-1 NDE
45 | Vibration analysis program and oil tribology | Vibration: Monthly Oil: Quarterly | 17-4 Vibration | UTH Vibration
46 | High vibration trip
47 | Spare motor, impeller, and shaft and/or adequate contingency plans |  | 13-24 Fans and Blowers | UTH Fans and Blowers
ELECTRICAL PREVENTIVE MAINTENANCE
| MAIN POWER TRANSFORMERS (3000 KVA & over) | FREQUENCY
52 | Oil tests for dielectric breakdown strength, power factor, moisture, interfacial tension, neutralization number & color | Annually | 5-4 Transformers | UTH Transformers | Maintaining Power for Productivity
53 | Dissolved Gas in Oil Analysis (DGA) | Annually |  | UTH Dissolved Gas Analysis
54 | Transformer winding and bushing power factor, turns ratio for onload tap changers, windings resistance, insulation resistance, polarization index (PI) testing. Only applies to 5,000-kVA and larger | 3 yrs | 5-10 Protective Grounding | UTH Power Factor Testing
55 | Bushing visual inspections (H.V. & L.V.) | Annually |  | UTH Service Interuption
56 | Proper interpretation of test results with plan of action on poor results
57 | Formalized plans to replace "PCB" contaminated equipment
| SWITCHGEAR | FREQUENCY
60 | Infra-red (thermography) survey | Annually | 5-20 Electrical Testing | UTH Infrared Testing | Maintaining Power for Productivity
60 | Relay testing & calibration | 3 yrs | 5-19 Switchgear & Circuit Breakers | UTH Overvoltage Tests | UTH Ground Fault Protection
62 | Switchgear and breaker testing (functional test, insulation resistance, contact resistance, lubrication, etc) | 3 yrs | 5-10 Protective Grounding | UTH Circuit Breaker Testing
63 | Fault current study completed and up to date |  | 5-18 Protection of Electrical Equip | UTH Coordination Study
64 | Proper interpretation of test results with plan of action on poor results |  |  | UTH Service Interuption
CABLES
67 | Cable tray debris removal |  | 5-20 Electrical Testing | UTH Ground Fault Protection
| MOTORS (600-HP/447-kW and greater with ratings of 2,300 V or greater) | FREQUENCY
70 | Dielectric Absorption/Polarization Index (PI) test, Power Facotr (PF) test, DC Conductivity test | 3 yrs | 5-17 Motors | UTH Electrical Testing of Motors | Maintaining Power for Productivity
71 | Clean air cooling vents & filters | Based on Operating Conditions | 5-18 Protection of Electrical Equip | UTH Ground Fault Protection
72 | Proper interpretation of test results with plan of action on poor results |  | 5-20 Electrical Testing | UTH Overvoltage Tests
| BATTERIES | FREQUENCY
75 | Battery PM to include cleaning connections, electrolite levels, specific gravity, and cell voltage | Monthly, Quarterly and Annually per DS 5-19, Table 3. | 5-20 Electrical Testing | UTH VRLA | Maintaining Power for Productivity
76 | Capacity testing | VRLA: Annually Flooded Lead Acid and Ni-Cd: 5 yrs | 5-19 Switchgear & Circuit Breakers
77 | Batteries designed for application (no vehicle batteries)
78 | Maintain chargers in working order
79 | Replace obsolete battery systems
| INDOOR SUBSTATIONS | FREQUENCY
82 | Ensure all cabinets are closed & indicating lights (red & green) are operable | Monthly | 5-19 Switchgear & Circuit Breakers | UTH Service Interuption | Maintaining Power for Productivity
83 | Seal all openings to switchgear cabinets |  | 5-20 Electrical Testing
84 | Provide clean-cool air to switchgear
| OUTDOOR MAIN SUBSTATIONS | FREQUENCY
87 | Lock all overhead structure switch disconnect extension rods to prevent accidental switching |  | 5-19 Switchgear & Circuit Breakers | UTH Service Interuption | Maintaining Power for Productivity
88 | Control weed growth and dust accumulation in substation |  | 5-20 Electrical Testing
89 | Clean bushings, insulators and connections | Annually
90 | Provide barriers/locks to keep unauthorized personnel out
Note on B10: Alignment of a kiln is critical to its proper operation. This will substantially reduce wear and stress on gears and bearings. Frequency: Kiln alignment should be performed every two years.
Note on B11: Shell profile will detect ovality problems in the shell and gives data on the adjustments required for proper operation. This will substantially reduce wear and stress on gears and bearings. Frequency: Ovality should be performed annually.
Note on B12: Non-destructive examination (NDE) will detect cracks in teeth and prove the condition of entire gear or shaft. The decision to repair will depend on the depth of the crack and how fast it is growing. The eddy current method requires no gear cleaning and can be done for about $8000 per gear. Dye penetrant, wet fluorescent magnetic particle and ultrasonic testing is also acceptable. Frequency: 3 years.
Note on B13: The auxiliary drive must be available in case of power loss or main drive failure to prevent shell overheating. There should be a separate auxiliary motor to drive the kiln in case of motor failure and not merely a backup generator. The auxiliary drive should be tested weekly.
Note on B14: The replacement of a ring gear can take many months and come at a high cost. A spare ring gear on site will mitigate downtime considerably. As an alternative, a formal written contingency plan to include welding procedures (if gear is weldable), companion spare located at another Cemex plant, a companion spare located at a competitors plant and/or a blank spare that would need machining. An old gear that has been refurbished will count as a viable spare.
Note on B15: The replacement of a riding ring can take many months and come at a significant cost. A spare riding ring will mitigate downtime considerably. As an alternative, a formal written contingency plan to include welding procedures should be formulated.
Note on B16: The main drive and pinions should be spared. As an alternative, a formal written contingency plan should be developed plan covering their accessibility through vendors or another Cemex plant and list repair organizations with the capabilities to perform repairs.
Note on B17: Temperature indication should be installed on the trunnion bearings of the kiln and can be direct reading or the preferred method of thermocouples with central room read outs and alarms.
Note on B18: Thermocouples with a control room readout and alarm should be installed on the drive gearbox along with low oil pressure indication switches for continuous flow oil systems.
Note on B19: Operators should be continuously trained to follow normal operations and emergency operating procedures. They should be aware of the hazards of not following procedures. Keep operating instructions for light-off and shut down in the control room.
Note on B22: This program should be administered by a reliability engineer who monitors and interprets results. Vibration analysis should be performed weekly where manual (hand-held) only is used and oil samples should be taken at least quarterly for critical equipment. Where there is an online fixed vibration monitoring system there is no need to conduct the weekly manual monitoring, only to keep weekly records.
Note on B23: Gears, like other mechanical parts, cannot survive indefinitely. Visual inspections compliment the oil analysis and vibration analysis programs. These inspections typically include tooth backlash and profile measurements. This should be done on a 3 year interval considering that there is a a good predictive maintenance (weekly vibration monitoring and quarterly oil analysis) otherwise this frequency can be increased.
Note on B24: Reliability programs ensure the longevity of gearboxes; however, sudden failures can not be detected. A vibration trip will act as a last line of defense and minimize the resulting damage in the event of a failure.
Note on B25: Non destructive examination (NDE) can help prevent unplanned downtime with the early detection of cracks. If discovered in the early stages, temporary repairs can be made and the equipment can continue to run while replacement parts are ordered. Cracks can also be monitored for continued growth while waiting for an opportunity for an outage to replace parts. If a crack grows to failure, the impact could be extensive physical damage and subsequent downtime. Frequency: 3 years.
Note on B26: High temperature alarm and trip should be installed on the bearings of high-speed enclosed gearboxes critical to production.The alarms and trips can be direct reading or with control room readouts.
Note on B27: High oil temperature, low oil pressure and low oil level protective devices capable of sending alarms and trips should be installed for high-speed enclosed gearboxes critical to production. Alarms can be local or to a control room with readouts.
Note on B28: These components should be spared to mitigate downtime or a formal written contingency plan should be in place that would minimize downtime in the event of failure. A formal written contingency plan should cover their accessibility through vendors or another Cemex plant and list repair organizations with the capabilities to perform repairs.
Note on B31: This program should be administered by a reliability engineer who monitors and interprets results. Vibration analysis should be performed weekly where manual (hand-held) only is used and oil samples should be taken at least quarterly for critical equipment. Where there is an online fixed vibration monitoring system there is no need to conduct the weekly manual monitoring, only to keep weekly records.
Note on B32: Gears, like other mechanical parts, cannot survive indefinitely. Visual inspections compliment the oil analysis and vibration analysis programs. These inspections typically include tooth backlash and profile measurements. This should be done on a 3 year interval considering that there is a a good predictive maintenance (weekly vibration monitoring and quarterly oil analysis) otherwise this frequency can be increased.
Note on B33: Reliability programs ensure the longevity of gearboxes; however, sudden failures can not be detected. A vibration trip will act as a last line of defense and minimize the resulting damage in the event of a failure.
Note on B34: Non destructive examination (NDE) can help prevent unplanned downtime with the early detection of cracks. If discovered in the early stages, temporary repairs can be made and the equipment can continue to run while replacement parts are ordered. Cracks can also be monitored for continued growth while waiting for an opportunity for an outage to replace parts. If a crack grows to failure, the impact could be extensive physical damage and subsequent downtime. Frequency: 3 years.
Note on B35: High temperature alarm and trip should be installed on the bearings of high-speed enclosed gearboxes critical to production.The alarms and trips can be direct reading or with control room readouts.
Note on B36: High oil temperature, low oil pressure and low oil level protective devices capable of sending alarms and trips should be installed for high-speed enclosed gearboxes critical to production. Alarms can be local or to a control room with readouts.
Note on B37: These components should be spared to mitigate downtime or a formal written contingency plan should be in place that would minimize downtime in the event of failure. A formal written contingency plan should cover their accessibility through vendors or another Cemex plant and list repair organizations with the capabilities to perform repairs.
Note on B40: A good percentage of losses can be traced back to poor housekeeping in substations. Good housekeeping is considered “Good Engineering Practice,” and there is no data sheet to reference. It can be a cultural problem, which has to be dealt with at the top management level. It must be stressed that each employee must take pride in their workplace. Electrical rooms should be clear of combustible materials and should not be used as storage areas. If dust ingress is a problem, actions should be taken to keep dust out or more frequent cleaning will be necessary. Extreme temperatures will reduce the life of insulation materials.
Note on B41: Cement product can find its way into bearing surfaces and can damage bearing and operating equipment.
Note on B44: Non-destructive examination (NDE) is vital on these hard working fans. Due to fouling, stresses are built up in the fan blades and hubs which can initiate cracks that could propagate to failure as well as unbalance. Frequency: 2 years
Note on B45: This program should be administered by a reliability engineer who monitors and interprets results. Vibration analysis should be performed monthly and oil samples should be taken at least quarterly.
Note on B46: Reliability programs ensure the longevity of bearings and the fan itself; however, sudden failures can not be detected. A vibration trip will act a last line of defense and minimize damage in the event of a failure.
Note on B47: These components should be spared to mitigate downtime or a formal written contingency plan should be in place that would minimize downtime in the event of failure. A formal written contingency plan should cover their accessibility through vendors or another Cemex plant and list repair organizations with the capabilities to perform repairs.
Note on B52: Oil screen testing can determine the insulation quality of the dielectric fluid. FM Global uses IEEE C57.106 standards for test results. Frequency: Annually.
Note on B53: Abnormalities within transformers release energy, which breaks down the oil molecule and forms gases that mostly remain, dissolved in the oil. Often the origin and nature of the defect can be determined from the type and quantity of various hydrocarbon gases found through the dissolved gas analysis (DGA). Gas analysis is used to detect problems such as corona discharge, arcing, overheating, overloading, low-energy sparking, etc., which may be taking place within the transformer.
Note on B54: Power Factor and Capacitance Purpose: Power factor and capacitance measurement is used to determine the condition of the capacitive insulation between the windings, and between the windings and the core and tank. It can detect contamination of the winding insulation by moisture, carbon, and other material. his test can also be applied to the bushings to determine the condition of condenser-type bushings. It can also detect contamination as well as deterioration of the capacitive layers in the bushing. Insulation Resistance Purpose: This test is performed by applying a DC voltage and measuring the leakage current to determine if the transformer insulation is dry and clean. The test can also pick up any unintentional grounds. Polarization Index Another insulation ratio used is the polarization index, which is a ratio of the 10-minute insulation reading to the 60-second insulation reading. A polarization index less than 1 indicates a wet or contaminated insulation. A polarization index greater than 2 indicates dry and clean insulation. Winding Resistance Purpose: This detects shorted turns, poor connections, open circuited windings and problems with the tap changer connections. Winding resistance is measured using a low resistance ohmmeter (Ductor®). Turns Ratio for On-Load Tap Changers Purpose: To detect shorted turns, open circuited windings, and tap changer problems. The turns-ratio test is performed using a special test set. A known low voltage is applied to the primary winding and the induced voltage is measured on the secondary winding. In a three winding transformer, the induced voltage on the tertiary winding is also measured. The test is performed one phase at a time. The measured turns-ratio should be within 0.5% of the nameplate value.
Note on B55: Annual visual inspections shoould be performed to check for cracked porcelain and a power factor test to prove the internal mechanisms.
Note on B56: Results must be reviewed to be useful. The testing program should include responsibility for review and analysis of results. Proper corrective actions should be taken.
Note on B57: PCB contaminated transformers and other electrical equipment can significantly impact the property damage and business interruption downtime in the event of an equipment failure or fire involving the contaminated equipment. It is very difficult to predict the increased severity of loss that could occur as it is very dependent on the nature of the event and where the PCBs spread. Before any recovery or restoration can begin, the PCBs must be abated and cleaned up. This can take days to sometimes weeks.
Note on B60: All electrical devices generate heat during normal operation. Infra-red is an effective tool for identifying high temperature before breakdown or fire occurs. This test will easily pay for itself in energy savings and unplanned downtime. Frequency: Annually.
Note on B61: Relays are designed to see an electrical fault and signal a tripping device that shuts down the flow of electricity (open breaker). If these devices are not tested and calibrated to trip a breaker in a coordinated function, then the upstream equipment can fail violently. Frequency: 3 years.
Note on B62: Failure of a protective device suchs as a circuit breaker, switches and fuses to operate and open the electrical circuit during an overload, electrical fault or other abnormal operating condition can trigger the following reactions: overheated electrical insulation, severe arcing, equipment damage, loss of power, production interruption and even fire. Frequency: 3 years.
Note on B63: If the available fault current is greater than the interrupting devices capability, the interrupting device will fail violently. When significant changes are made in the plant or when there are changes in the utility feed and/or transformers, the available fault current will change. The fault current study will allow a comparison of the available fault current with installed circuit breaker ratings. If these ratings are exceeded, breakers will need to be replaced or fault current limiting fuses can be installed. Even when there are no apparent changes, this should be updated every 10 years.
Note on B64: Results must be reviewed to be useful. The testing program should include responsibility for review and analysis of results. Proper corrective actions should be taken.
Note on B67: Suspended cable trays can collapse if build up of debris is left unchecked.
Note on B70: The number of tests can increase or decrease and this will depend on condition-monitoring data, results of routine inspections, operating experience, and failure history. The majority of the large critical drive motors are subjected to a very dirty atmosphere in a cement plant. This dirt build up will cause abrasive conditions in the stator winding with ultimate failure. The dielectric absorption test is also referred to as the polarization index (PI) test. This is a ratio of the insulation resistance readings taken at 1 minute and 10 minutes. Power Factor detected failure mode: Ground wall insulation deterioration due to thermal degradation or water ingress. DC Conductivity failure mode: Broken and cracked windings, poor connections, shorted turns in rotor winding Frequency: 3 years.
Note on B71: Heat dissipation in an enclosed motor is very important to ensure proper operation of the motor. Clogged vents and filters can cause overheating and rapid deterioration of the windings. Frequency: Based on operating conditions.
Note on B72: Results must be reviewed to be useful. The testing program should include responsibility for review and analysis of results. Proper corrective actions should be taken with documentation.
Note on B75: Flooded Lead Acid. Monthly: Check and record charger voltage and current. Check electrolyte levels and for evidence of corrosion and leaks Quarterly: In addition to monthly inspection, check the specific gravity and the temperature of 10 of the cells. Check the individual cell voltages of all cells. Annually: In addition to quarterly inspection, check the specific gravity of all the cells, as well as all inter-cell resistances. Flooded Ni-Cd. Monthly: Check and record charger voltage and current. Check electrolyte levels, and for evidence of corrosion and leaks. Quarterly: In addition to monthly inspection, check pilot cell electrolyte temperatures. Annually: In addition to quarterly inspection, check all inter-cell resistances. VRLA. Monthly: Check and record charger voltage and current. Check ambient temperature, and for evidence of corrosion, leaks, overheating, and distorted cases. Quarterly: In addition to monthly inspection, check the internal cell resistance and negative terminal temperature of 10 of the cells. Check the individual cell voltages of all cells. Annually: In addition to quarterly inspection, check the inter-cell resistances and the amount of ripple in the charger waveform.
Note on B76: Testing of valve regulated lead acid (VLRA) type batteries should be done at least annually due to the premature failure rate. The more durable flooded cell lead acid and Ni-Cd batteries can be tested on a 5 year frequency. High ambient temperatures in the battery room (>25ºC) will require more frequent testing. This will need evaluation on a case by case basis.
Note on B77: At times, vehicle batteries are used to ensure that control power is available when existing batteries are found to have failed. Only batteries designed for this application should be used. Vehicle batteries aren't designed for this service and will only last about three years.
Note on B78: Typically, control power is supplied though the charger and then through the batteries when the charger is off-line. Batteries will completely discharge in a few days. Defective chargers should be replaced or repaired to ensure the integrity of battery bank.
Note on B79: Obsolete batteries can cause significant losses if control power is not available to operate circuit breakers. Replace these batteries at any sign of internal damage, cracked casings or severe overheating. In extreme cases damaged batteries can result in explosions. Debris buildup in the bottom of the cells and warped plates are signs that the batteries are at the end of their life.
Note on B82: Indicating lights (red/green) are important to any well operated substation. They give the status of the breaker and indicate that there is power to the tripping coil. Cabinet doors should remain closed to keep out dust and animals. Frequency: Monthly rounds by Electrician.
Note on B83: Openings invite animals and allow the entry of dust and moisture.
Note on B84: Many electrical failures are caused by overheating above the designed rating. This substantially reduces the life of insulation systems. All substations should be enclosed and provided positive air and air conditioning. This keeps out contamination from the process and increases the reliability of switchgear.
Note on B87: Outdoor substations are usually equipped with aerial switches for disconnecting line power. The overhead disconnects are operated via extension rods. These are provided with locking mechanisms that will accept a padlock.
Note on B88: The substrate in a substation is designed to contain spilled oil and protect the grounding grid. Dust accumulations and weed growth defeats the purpose and can also cause cooling problems with equipment.
Note on B89: Annual cleaning of the main substations is a requirement due to the dirty operating environment (surrounding process). Frequency: Annually or more often if needed.

## DS Links
Data Sheet | Title
5-4 | Transformers
5-19 | Switchgear and Circuit Breakers
5-20 | Electrical Testing
5-28 | DC Battery Systems
13-7 | Gears
9-0 | Asset Integrity

## Transformers ITM Recorder
Electrical
Transformers >5 MVA
Data Sheet
# | Section | Table | Appendix |  |  |  | Cont. | W | M | Q | S/A | A | x YRS | Other (describe)
5-4
|  |  |  | Online: |  | Visual
IR
DGA/O
[5 empty] | Testing: | PD
etc.
Offline:
Ins. Res
Transformers <5 MVA
# | Section | Table | Appendix |  |  |  | Cont. | W | M | Q | S/A | A | x YRS | Other (describe)
5-20 |  |  |  | Online: |  | Visual
IR
DGA/O
[5 empty] | Testing: | PD
etc.
Offline:
Ins. Res

## Switchgear ITM Recorder
Electrical
MV Swgr
# | Section | Table | Appendix |  |  | Cont. | W | M | Q | S/A | A | x YRS | Other (describe)
5-19 |  |  |  | Online: | Visual
IR
PD
C/C/D/T
Offline:
Ins. Res
Contact R
t&c volt.
travel
etc.
LV Swgr
# | Section | Table | Appendix |  |  | Cont. | W | M | Q | S/A | A | x YRS | Other (describe)
5-20 |  |  |  | Online: | Visual
IR
PD
C/C/D/T
# | Section | Table | Appendix |  |  | Cont. | W | M | Q | S/A | A | x YRS | Other (describe)
Offline:
Ins. Res
Contact R
t&c volt.
travel
etc.

## Motor ITM Recorder
Electrical
Motors >500 HP
Data Sheet
# | Section | Table | Appendix |  |  |  | Cont. | W | M | Q | S/A | A | x YRS | Other (describe)
5-4 |  |  |  | Online: |  | Visual
IR
DGA/O
[5 empty] | Testing: | PD
etc.
Offline:
Ins. Res
Critical Spares
A. AC Motors (5000 hp [3700 kW] and larger):
Data Sheet
# | Section | Part |  |  |  | What | [5 empty] | Yes | No | Other (describe)
5-17 | 2.5.1 | A
A complete stator or complete set of stator coils
For synchronous motors, a complete rotor, or sufficient rotor coils and field poles as specified by the manufacturer
A complete set of bearings
B. DC Motors (3000 hp [2200 kW] and larger)
Data Sheet
# | Section | Part |  |  |  | What | [5 empty] | Yes | No | Other (describe)
5-17 | 2.5.1 | A
A complete armature (including commutator)
Sufficient field pole windings (e.g., shunt, series, interpole) to replace one quarter of the motor field
A complete set of bearings

## Table 6a
Table 6a AC Induction Motors
Component | Test | Dismantles | Inspections
Stator Windings | Insulation Resistance (IR) | X | X
| Polarization Index (PI) | X | X
| DC Conductivity | X | X
| Power Factor (PF) | X | X
| Power Factor Tip Up | X | X
| Partial Discharge 1 | X | X
Stator Core | Visual inspection for hot spots | X | X
| Air gap measurement | X
Rotor Winding | Loop Test | X | X
| Insulation Resistance 2 | X | X
| Polarization Index (PI) 2 | X | X
| DC Conductivity Test 2 | X | X
| Surge Companson or Recurrent Surge Oscillograph 2 | X
| Growler Test3 | X
| Inspect slip rings, brushes and brush rigging for wear and damage 2 | X | X
Retaining Rings 4 | Visual inspection for corrosion | X | X
| NDE with ring in-situ | X
| NDE with ring removed | X
Rotor Fans | Visual Inspection for cracking | X | X
| NDE of fan blades and vanes for cracking | X
Rotor Forging | Visual inspection for cracking | X | X
| NDE of forging for cracks and inclusions | X
| Proper alignment of motors and driven objects | X
Bearings | Insulation resistance 5 | X | X
| Inspect white metal surfaces of sleeve bearings | X
| Inspect cage and rolling elements of antifriction bearings | X
| Inspect shaft surfaces in contact with bearings | X
Coolers 6 | Inspect air/water heat exchangers for tube erosion or corrosion | X
| Inspect and clean air filters on air cooled motors | X | X
RTD orTC | Check condition of RTD | X
| Measure RTD/TC resistance and continuity | X
Heater | Check that the motor heater is functioning properly | X | X

## Table 6b
Component | Test | Dismantles | Inspections
Stator Windings | Insulation Resistance (IR) | X | X
| Polarization Index (PI) | X | X
| DC conductivity | X | X
| Power Factor (PF) | X | X
| Power Factor Tip Up | X | X
| Partial Discharge 1 | X | X
Stator Core | Visual inspection for hot spots | X | X
| Air gap measurement | X
| Loop Test | X
Rotor Winding 2 | Insulation Resistance | X | X
| Polarization Index (PI) | X | X
| DC Conductivity Test | X | X
| Inspect slip rings, brushes and brush rigging for wear and damage | X | X
| DC Volt Drop test across each pole 3 | X
| Check inter-pole connections for cracking overheating and damage 3 | X
| Measure inter-pole connection resistance 3 | X
| Check inter-pole connection bracing and poles for distortion 3 | X
| Surge Comparison or Recurrent Surge Oscillograph 4 | X
Retaining Rings5 | Visual inspection for corrosion | X | X
| NDE with ring in-situ | X
| NDE with ring removed | X
Rotor Fans | Visual Inspection for cracking | X | X
| NDE of fan blades and vanes for cracking | X
Rotor Forging | Visual inspection for cracking | X | X
| NDE of forging for cracks and inclusions | X
| Proper alignment of motors and driven objects | X
Bearings | Insulation resistance 4 | X | X
| Inspect white metal surfaces of sleeve bearings | X
| Inspect cage and rolling elements of antifriction bearings | X
| Inspect shaft surfaces in contact with bearings | X
Coolers 6 | Inspect air/water heat exchangers for tube erosion or corrosion | X
| Inspect and clean air filters on air cooled motors | X | X
RTD or TC | Check condition of RTD | X
| Measure RTD/TC resistance and continuity | X
Heater | Check that the motor heater is functioning properly | X | X
Static Exciter | Visual inspection for cleanliness and condition | X
| Check rectifier integrity | X
Rotating Exciter | Visual inspection for cleanliness and condition | X | X
| Perform IR, PI, DC and PF tests on exciter windings | X
| Check diode integrity | X
Brushless Exciter | Visual inspection for cleanliness and condition | X | X
| Perform IR, PL DC and PF tests on exciter windings | X
| Check diode integrity | X
Table 6b: AC synchronous motors (round rotor and salient rotor)
1 Only if the motor voltage is 4 kV and higher
2 Include damper (amortisseur) bindings
3 Applicable to saSent pole synchronous motors
4 Only applicable to cyindrical pole synchronous motors
5 Only applicable //here an air/water heat exchanger is provided

## Table 6c
Component | Test | Dismantles | Inspections
Field (Stator) | Inspect inter-pole connections for cracking and damaging | X
windings 1 | Insulation Resistance (IR) | X
| Polarization Index (PI) | X | X
| DC conductivity (DC) | X | X
| DC voltage drop test across each field pole | X | X
| DC polarity check across each field pole | X | X
Core and pole | Visual inspection for hot spots | X | X
pieces | Air gap measurement | X
Armature (rotor) | Insulation Resistance | X | X
Winding | Polarization Index (PI) | X | X
| DC Conductivity Test | X | X
Commutator | Visual inspection for streaking, unevenness, burning and etching | X | X
| Perform commutator run-out measurement | X
| Check brushes and brush rigging for wear and damage | X | X
Rotor Fans | Visual Inspection for cracking | X | X
| NDE of fan blades and vanes for cracking | X
Rotor Forging | Visual inspection for cracking | X | X
| NDE of forging for cracks and inclusions |  | X
| Proper alignment of motors and driven objects | X
Bearings | Insulation resistance 2 | X | X
| Inspect white metal surfaces of sleeve bearings | X
| Inspect cage and rolling elements of antifriction bearings | X
| Inspect shaft surfaces in contact with bearings | X
Coolers 3 | Inspect air/water heat exchangers for tube erosion or corrosionco | X
| Inspect and clean air filters on air cooled motors | X | X
RTD or TC | Check condition of RTD | X
| Measure RTD/TC resistance and continuity | X
Heater | Check that the motor heater is functioning properly | X | X
Table 6c: DC Motors
1 Include non-power field windings in the test (interpoles, commutating and compensating windings)
2 Only applicable for insulated bearings
3 Only applicable where an air/water heat exchanger is provided

## Battery ITM Recorder
Electrical
Transformers >5 MVA
Data Sheet
# | Section | Table | Appendix |  |  |  | Cont. | W | M | Q | S/A | A | x YRS | Other (describe)
5-4 |  |  |  | Online: |  | Visual
IR
DGA/O
[5 empty] | Testing: | PD
etc.
Offline:
Ins. Res
Transformers <5 MVA
# | Section | Table | Appendix |  |  |  | Cont. | W | M | Q | S/A | A | x YRS | Other (describe)
5-20 |  |  |  | Online: |  | Visual
IR
DGA/O
[5 empty] | Testing: | PD
etc.
Offline:
Ins. Res
MV Swgr
# | Section | Table | Appendix |  |  |  | Cont. | W | M | Q | S/A | A | x YRS | Other (describe)
5-19 |  |  |  | Online: |  | Visual
IR
PD
C/C/D/T
Offline:
Ins. Res
Contact R
t&c volt.
travel
etc.
BATTERIES - MV Swgr
# | Section | Table | Appendix |  |  |  | Cont. | W | M | Q | S/A | A | x YRS | Other (describe)
5-28 |  |  |  | Online: |  | Visual
IR
Temp
Alarms
[6 empty] | Remote Monitoring | Y | N | [5 empty] | what?
[6 empty] | BMS | Y | N | [5 empty] | what?
Offline:
inter-cell
conductance
capacity
etc.
LV Swgr
# | Section | Table | Appendix |  |  |  | Cont. | W | M | Q | S/A | A | x YRS | Other (describe)
5-20 |  |  |  | Online: |  | Visual
IR
PD
C/C/D/T
# | Section | Table | Appendix |  |  |  | Cont. | W | M | Q | S/A | A | x YRS | Other (describe)
Offline:
Ins. Res
Contact R
t&c volt.
travel
etc.
Mills
# | Section | Table | Appendix |  |  |  | Cont. | W | M | Q | S/A | A | x YRS | Other (describe)
Design:
Diameter x Length
|  |  |  | motor | HP
kW
RPM
|  |  |  | Mill | RPM
|  |  |  | Max | TPH
|  |  |  | Avg | TPH
|  |  |  | Spares/ECP | [9 empty] | Spares Comments
[6 empty] | Motor | Y | N | Ratings -->
[6 empty] | Pinions | Y | N
[6 empty] | Ring Gear | Y | N | Ratings -->
[6 empty] | Bearings | Y | N
[6 empty] | ECP | Y | N | Viable | Details -->
|  |  |  | ITM (General) |  |  | Y | N | M | Q | S/A | A | x YRS
Temp Gun
IR
NDE
[7 empty] | Cont. | W | M | Q | S/A | A | x YRS
|  |  |  | Lube Oil |  | Ring Gear
Motor Bearings
Vibration Analysis
Controls & Safety Devices
Ring Gear
Strob
Temp Gun
IR
L/O
Lining
Slurry Racing
[6 empty] | Charge Monitoring | [7 empty] | monitoring via the motor kW. One re-start allowed only, then troubleshoot/inspect; must be cleared by OPS Mech. & Elec. personnel prior to additional starts.
[6 empty] | Mill Reversable Directions | Y | N | Freq -->
|  |  |  | Motor |  |  | A | 3 yr | 6 yr | Other
[6 empty] | Inspection | [7 empty] | Inspection - 3 yr
[6 empty] | Dismantle | [7 empty] | Dismantle - 6 yr
[5 empty] | Type | Induction | (6a)
[5 empty] | Type | Synchronous | (6b)
[5 empty] | Type | DC | (6c)
|  |  |  | L/O |  | Sample Freq. | H | Shift | W | M | Q | S/A | A C/O | L/O: Quarterly samples C/O=changeout
|  |  |  | L/O | (Local Only) |  | Y | N
[6 empty] | Temp (T) | Y | N
[6 empty] | Press (P) | Y | N
[6 empty] | Flow (F) | Y | N
[6 empty] | Alarm (Warning) | Y | N
[6 empty] | Alarm (High) | Y | N
[6 empty] | Trip | Y | N
|  |  |  | C&SD | [9 empty] | C&SD: - Motor bearings: T - Mill bearing L/O: T, P, F - Motor kW - Motor O/C - Vibration analysis - Monitoring by Mill Control
[5 empty] | Motor | Bearings | T
[5 empty] | Motor | Bearing L/O | T | P | F
[5 empty] | Motor | kW | Y | N
[5 empty] | Motor | O/C | Y | N
[5 empty] | Motor | Vibration Analysis | Y | N | Cont. | W | M | Other -->
[5 empty] | Motor | Remote Monitoring | Y | N |  |  |  | Who? -->
|  |  |  | Ring Gear |  | Vibration Analysis | Y | N | Cont. | W |  | Other -->
|  |  |  | Ring Gear |  | L/O | Y | N | Shift | H | D | W | M
|  |  |  | NDE | Last Date:
[5 empty] | Prev. Date: | Y: Previous Date Performed
[15 empty] | Ball Mill | SAG Mill
[15 empty] | Design: Size: 11 ft. dia. x 13 ft. Motor: 900 HP Mill RPM: [unk] TPH (Max): 120 TPH TPH (Used/Avg): 100 TPH Ring Gear (Cast or Forged): Cast Ring Gear Reversable?: [unk] Rotation Reversal: N/A Motor Design: HP: 900 hp RPM: 897 rpm FLA: 114 Amps Voltage: 4.16 kV Phase(s): 3 phases Freq: 60 Hz Relays (ANSI #s): Spares: - Pinion gears - Motor - ring gear (forged or cast?) - bearings ITM: Temp Monitoring: - Temp gun: every shift Vib - continuous NDE: Annual UT (Metzo); tracking/trending cracks (in-progress) C&SD: Annual Ring Gear: - Visuals: - Walkdown: Shift - Strobe inspection: Shift - Temp gun: Shift - Lube Oil visual - every shift - IR scan: No. Discussed w/ site and showed examples - Lining (PIN Profile) - Quarterly, replacements every 24 mo - Slurry racing inspections - Charge monitoring - via kW NDE: Type: UT Objects: trunnion (feed and disch.), ring gear, pinion, segment bolts Indications: Yes Last performed: 4/2023 Continuous Monitoring: - Vibration: motor - Temperature: bearings, L/O, ring gear L/O - Pressure, Flow: bearing L/O Additional Eqpt Notes: Final Drive Pinion - inst Extra History: - Updated RV to $7.8 M per EVG | Design: Size: 11 ft. dia. x 13 ft. Motor: 900 HP Mill RPM: [unk] TPH (Max): 120 TPH TPH (Used/Avg): 100 TPH Ring Gear (Cast or Forged): Cast Ring Gear Reversable?: [unk] Rotation Reversal: N/A Motor Design: HP: 900 hp RPM: 897 rpm FLA: 114 Amps Voltage: 4.16 kV Phase(s): 3 phases Freq: 60 Hz Relays (ANSI #s): Spares: - Pinion gears - Motor - ring gear (forged or cast?) - bearings ITM: Temp Monitoring: - Temp gun: every shift Vib - continuous NDE: Annual UT (Metzo); tracking/trending cracks (in-progress) C&SD: Annual Ring Gear: - Visuals: - Walkdown: Shift - Strobe inspection: Shift - Temp gun: Shift - Lube Oil visual - every shift - IR scan: No. Discussed w/ site and showed examples - Lining (PIN Profile) - Monthly profiles, replacements 4-6 mo (belly), 8 mo feed/disch, rest 12 -18 mo, as needed. - Slurry racing inspections - Charge monitoring - via kW NDE: Type: UT Objects: trunnion (feed and disch.), ring gear, pinion, segment bolts Indications: Yes Last performed: 4/2023 Continuous Monitoring: - Vibration: motor - Temperature: bearings, L/O, ring gear L/O - Pressure, Flow: bearing L/O Additional Eqpt Notes: Final Drive Pinion - inst Extra History: - Updated RV to $7.8 M per EVG

## Mill ITM Recorder
Mills
# | Section | Table | Appendix |  |  |  | Cont. | W | M | Q | S/A | A | x YRS | Other (describe)
Design:
Diameter x Length
|  |  |  | motor | HP
kW
RPM
|  |  |  | Mill | RPM
|  |  |  | Max | TPH
|  |  |  | Avg | TPH
|  |  |  | Spares/ECP | [9 empty] | Spares Comments
[6 empty] | Motor | Y | N | Ratings -->
[6 empty] | Pinions | Y | N
[6 empty] | Ring Gear | Y | N | Ratings -->
[6 empty] | Bearings | Y | N
[6 empty] | ECP | Y | N | Viable | Details -->
|  |  |  | ITM (General) |  |  | Y | N | M | Q | S/A | A | x YRS
Temp Gun
IR
NDE
[7 empty] | Cont. | W | M | Q | S/A | A | x YRS
|  |  |  | Lube Oil |  | Ring Gear
Motor Bearings
Vibration Analysis
Controls & Safety Devices
Ring Gear
Strob
Temp Gun
IR
L/O
Lining
Slurry Racing
[6 empty] | Charge Monitoring | [7 empty] | monitoring via the motor kW. One re-start allowed only, then troubleshoot/inspect; must be cleared by OPS Mech. & Elec. personnel prior to additional starts.
[6 empty] | Mill Reversable Directions | Y | N | Freq -->
|  |  |  | Motor |  |  | A | 3 yr | 6 yr | Other
[6 empty] | Inspection | [7 empty] | Inspection - 3 yr
[6 empty] | Dismantle | [7 empty] | Dismantle - 6 yr
[5 empty] | Type | Induction | (6a)
[5 empty] | Type | Synchronous | (6b)
[5 empty] | Type | DC | (6c)
|  |  |  | L/O |  | Sample Freq. | H | Shift | W | M | Q | S/A | A C/O | L/O: Quarterly samples C/O=changeout
|  |  |  | L/O | (Local Only) |  | Y | N
[6 empty] | Temp (T) | Y | N
[6 empty] | Press (P) | Y | N
[6 empty] | Flow (F) | Y | N
[6 empty] | Alarm (Warning) | Y | N
[6 empty] | Alarm (High) | Y | N
[6 empty] | Trip | Y | N
|  |  |  | C&SD | [9 empty] | C&SD: - Motor bearings: T - Mill bearing L/O: T, P, F - Motor kW - Motor O/C - Vibration analysis - Monitoring by Mill Control
[5 empty] | Motor | Bearings | T
[5 empty] | Motor | Bearing L/O | T | P | F
[5 empty] | Motor | kW | Y | N
[5 empty] | Motor | O/C | Y | N
[5 empty] | Motor | Vibration Analysis | Y | N | Cont. | W | M | Other -->
[5 empty] | Motor | Remote Monitoring | Y | N |  |  |  | Who? -->
|  |  |  | Ring Gear |  | Vibration Analysis | Y | N | Cont. | W |  | Other -->
|  |  |  | Ring Gear |  | L/O | Y | N | Shift | H | D | W | M
|  |  |  | NDE | Last Date:
[5 empty] | Prev. Date: | Y: Previous Date Performed
[15 empty] | Ball Mill | SAG Mill
[15 empty] | Design: Size: 11 ft. dia. x 13 ft. Motor: 900 HP Mill RPM: [unk] TPH (Max): 120 TPH TPH (Used/Avg): 100 TPH Ring Gear (Cast or Forged): Cast Ring Gear Reversable?: [unk] Rotation Reversal: N/A Motor Design: HP: 900 hp RPM: 897 rpm FLA: 114 Amps Voltage: 4.16 kV Phase(s): 3 phases Freq: 60 Hz Relays (ANSI #s): Spares: - Pinion gears - Motor - ring gear (forged or cast?) - bearings ITM: Temp Monitoring: - Temp gun: every shift Vib - continuous NDE: Annual UT (Metzo); tracking/trending cracks (in-progress) C&SD: Annual Ring Gear: - Visuals: - Walkdown: Shift - Strobe inspection: Shift - Temp gun: Shift - Lube Oil visual - every shift - IR scan: No. Discussed w/ site and showed examples - Lining (PIN Profile) - Quarterly, replacements every 24 mo - Slurry racing inspections - Charge monitoring - via kW NDE: Type: UT Objects: trunnion (feed and disch.), ring gear, pinion, segment bolts Indications: Yes Last performed: 4/2023 Continuous Monitoring: - Vibration: motor - Temperature: bearings, L/O, ring gear L/O - Pressure, Flow: bearing L/O Additional Eqpt Notes: Final Drive Pinion - inst Extra History: - Updated RV to $7.8 M per EVG | Design: Size: 11 ft. dia. x 13 ft. Motor: 900 HP Mill RPM: [unk] TPH (Max): 120 TPH TPH (Used/Avg): 100 TPH Ring Gear (Cast or Forged): Cast Ring Gear Reversable?: [unk] Rotation Reversal: N/A Motor Design: HP: 900 hp RPM: 897 rpm FLA: 114 Amps Voltage: 4.16 kV Phase(s): 3 phases Freq: 60 Hz Relays (ANSI #s): Spares: - Pinion gears - Motor - ring gear (forged or cast?) - bearings ITM: Temp Monitoring: - Temp gun: every shift Vib - continuous NDE: Annual UT (Metzo); tracking/trending cracks (in-progress) C&SD: Annual Ring Gear: - Visuals: - Walkdown: Shift - Strobe inspection: Shift - Temp gun: Shift - Lube Oil visual - every shift - IR scan: No. Discussed w/ site and showed examples - Lining (PIN Profile) - Monthly profiles, replacements 4-6 mo (belly), 8 mo feed/disch, rest 12 -18 mo, as needed. - Slurry racing inspections - Charge monitoring - via kW NDE: Type: UT Objects: trunnion (feed and disch.), ring gear, pinion, segment bolts Indications: Yes Last performed: 4/2023 Continuous Monitoring: - Vibration: motor - Temperature: bearings, L/O, ring gear L/O - Pressure, Flow: bearing L/O Additional Eqpt Notes: Final Drive Pinion - inst Extra History: - Updated RV to $7.8 M per EVG

## 13-17 Table 1
Table 1. Alarm and Trip Summary for Protective Systems
Protective System Device, Alarms and Trips | Alarm | Trip
Overspeed trip system:-Single-shaft-Multiple-shaft (each shaft)-Mechanical & electronic | x | x
Rotor thrust / axial position monitoring by axial proximity probes, or temperature in thrust bearing pads (see Note 4) | x | x
Low oil pressure sensor, main lube oil pump, activates standby pump | x
Low oil-pressure sensor, auxiliary lube-oil pump | x | x
Low oil-pressure sensor, emergency lube- oil pump | x
Emergency lube oil pump running | x
High lube oil filter differential pressure | x
Low oil-level sensor in lube oil tank (See Note 5) | x | x
High oil-level sensor in tank | x
High oil-temperature sensor, lube-oil header, supply or bearing drains | x | x
Turbine thrust bearing thermocouple, high temperature, metal temperature, and/or drain lube-oil temperature (For existing installations, an operational procedure in place if no trip is provided). (See Note 2) | x | x
Turbine bearing high temperature, thermocouples or embedded RTDs in all Babbitt bearings and/or thermocouple in the roller bearing oil drain lines. (For existing installations, an operational procedure in place if no trip is provided). (see Note 2) | x | x
Roller Bearing Chip Detectors (an operational procedure to immediately shutdown and inspect the source of the chips should be in place) | x
Vibration monitoring by fixed instrumentation or handheld device (includes a senior operations notification procedure) | x
High vibration instrumentation on bearings including the gearbox unit, exceeds set point (includes a senior operations notification procedure) (See Note 1) | x | x
High exhaust gas temperature | x | x
High turbine exhaust temperature spread/blade path spread | x | x
High turbine wheel space or disc-cavity temperature monitoring | x
Compressor bleed valve position error (failure to open on startup and shutdown, failure to remain closed at speed) |  | x
Inlet guide vane (IGV), variable stator vane (VSV), if equipped, position error/abnormal position feedback to DCS | x | x
Bleed heat anti-icing, if equipped, abnormal position feedback to DCS | x
Compressor Surge Protection (See Note 5.) |  | x
Dry Low NOx flash back temperature | x
High pressure differential across inlet air filter (run-back potential, if equipped) | x
Combustion flame monitoring/flame-out protection |  | x
Over and under fuel pressure protection |  | x
Air intake structure implosion protection | x
Dry Low NOx combustion dynamics | x | x
Hydraulic pressure low, auxiliary power unit for valve actuation |  | x
Note 1. Trip is based on absolute (casing) radial vibration.
Note 2. This recommendation is for turbines with hydrodynamic bearings (may include aeroderivative power turbines). A unit trip may be warranted depending on manufacturer specifications regarding bearing metal temperature limitations. Note 3. May be necessary due to bearing metal temperature limitations, notably on exhaust end bearings. Note 4. This recommendation is for turbines with hydrodynamic (sliding) bearings. A unit trip may be warranted depending on manufacturer specifications regarding operating clearance limitations. Note 5. Common for new state of the art F, G, H, J class gas turbines.